## Annexure-A
INDIAN INSTITUTE OF TECHNOLOGY KANPUR
NIT No. 20/Civil/D2/2020-21/03
Name of Work:- Making emergency exit on first floor with spiral fire escape and making concrete path for block B in pre engineered building near Flight lab. .
SCHEDULE OF QUANTITY
Item.No | Description of Items | Qty | Unit | Rate in Figures without GST in Rupees | Amount
1 | EARTH WORK
1.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m.
1.1.1 | All kinds of soil. | 16.56 | cum | 221.21 | 3663
1.2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 16.56 | cum | 192.59 | 3189
1.3 | Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m.
1.3.1 | All kinds of soil | 100 | sqm | 21.35 | 2135
2 | CONCRETE WORK
2.1 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :
2.1.1 | 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources). | 3.55 | cum | 5076.37 | 18021
3 | REINFORCED CEMENT CONCRETE
3.1 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, ifnishing and reinforcement- All work up to plinth level :
3.1.1 | 1:1.5:3 (1 cement: 1.5 coarse sand (zone-III) derived from natural sources: 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 1.46 | cum | 6767.42 | 9880
3.2 | Centering and shuttering including strutting, propping etc. and removal of form for
3.2.1 | Foundations, footings, bases of columns, etc. for mass concrete | 6.5 | sqm | 249.75 | 1623
3.3 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level.
3.3.1 | Thermo-Mechanically Treated bars of grade Fe-500D or more. | 115 | kg | 73.21 | 8419
4 | MASONRY WORK
4.1 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:
4.1.1 | Cement mortar 1:6 (1 cement : 6 coarse sand) | 5.81 | cum | 5398.9 | 31368
4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :
4.2.1 | Cement mortar 1:6 (1 cement : 6 coarse sand) | 5.18 | cum | 6655.37 | 34475
5 | CLADDING WORK
5.1 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including: (a) Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design. (b) Providing, fabricating and supplying and fixing panels of aluminium composite panel cladding in pan shape in metalic colour of approved shades made out of 4mm thick aluminium composite panel material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminium sheets (each 0.5mm thick). The aluminium composite panel cladding sheet shall be coil coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin coating of approved colour and shade on face # 1 and polymer (Service) coating on face # 2 as specified using stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc. (c) The fastening brackets of Aluminium alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labour component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminium composite panel cladding, cleaning and protection of the curtain wall with aluminium composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminium item.s The Contractor shall provide curtain wall with aluminium composite panel cladding, having all the performance characteristics all complete , as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places. | 7.2 | sqm | 3778.86 | 27208
6 | STEEL WORK
6.1 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.
6.1.1 | Hot finished seamless type tubes | 255 | kg | 138.09 | 35213
6.2 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required.
6.2.1 | In stringers, treads, landings etc. of stair cases, including use of chequered plate wherever required, all complete | 1336.9 | kg | 82.11 | 109773
6.2.2 | In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works | 1280 | kg | 114.86 | 147021
6.3 | Providing and fixing hand rail of approved size by welding etc. to steel ladder railing, balcony railing, staircase railing and similar works, including applying priming coat of approved steel primer.
6.3.1 | M.S. tube | 160 | kg | 127.7 | 20432
6.4 | Providing and fixing carbon steel galvanised ( minimum coating 5 micron) dash fastener of 10 mm dia double threaded 6.8 grade (yield strength 480 N/mm2), counter sunk head, comprising of 10 mm dia polyamide PA 6 grade sleeve, including drilling of hole in frame , concrete/ masonry, etc. as per direction of Engineer-in-charge.
6.4.1 | 10 x 120 mm | 136 | each | 117.71 | 16009
7 | FLOORING
7.1 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) :
7.1.1 | 25 mm thick | 20 | sqm | 1343.13 | 26863
8 | FINISHING
8.1 | 12 mm cement plaster of mix :
8.1.1 | 1:6 (1 cement: 6 coarse sand) | 35 | sqm | 231.08 | 8088
8.2 | 15 mm cement plaster on rough side of single or half brick wall of mix:
8.2.1 | 1:6 (1 cement: 6 coarse sand) | 25 | sqm | 266.46 | 6661
8.3 | Finishing walls with Acrylic Smooth exterior paint of required shade :
8.3.1 | New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 60 | sqm | 144.41 | 8665
8.4 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :
8.4.1 | Two or more coats on new work | 135 | sqm | 106.57 | 14387
9 | ROAD WORK
9.1 | Providing and laying design mix cement concrete of M-30 grade, in roads/ taxi tracks/ runways, using cement content as per design mix, using coarse sand and graded stone aggregate of 40 mm nominal size in appropriate proportions as per approved & specified design criteria, providing dowel bars with sleeve/ tie bars wherever required, laying at site, spreading and compacting mechanically by using needle and surface vibrators, levelling to required slope/ camber, finishing with required texture, including steel form work with sturdy M.S. channel sections, curing, making provision for contraction/ expansion, construction & longitudinal joints (10 mm wide x 50 mm deep) by groove cutting machine, providing and filling joints with approved joint filler and sealants, complete all as per direction of Engineer-in-charge (Item of joint fillers, sealants, dowel bars with sleeve/ tie bars to be paid separately). Note:- Cement content considered in M-30 is @ 340 kg/cum. Excess/ less cement used as per design mix is payable/ recoverable separately.
9.1.1 | Cement concrete manufactured in automatic batching plant (RMC plant) i/c transportation to site in transit mixer | 6.25 | cum | 8026.08 | 50163
10 | ALUMINIUM WORK
10.1 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) :
10.1.1 | For fixed portion
10.1.1.1 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | 20 | kg | 371.72 | 7434
| Total Estimated Cost without GST |  |  |  | 590690