## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: Minor rectification works in GH-1 and structural repair and painting works in toilets of all blocks of Hall - 5
NIT No: Civil/11/08/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component |  |  |  | 1 | Component
1.01 | FINISHING | item no.1 | [52 empty] | 1.01 | Supply installation testing and commissioning of cubical type LT panel-01 (IEC 61439 ) suitable for 4000Amp 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | item no.1 |  |  | 1.01 | FINISHING | item no.1
1.02 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification. | item no.2 | [52 empty] | 1.02 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser/meter (on all incomer and outgoing feeders) to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification. | item no.2 |  |  | 1.02 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification. | item no.2
1.03 | Two or more coats on new work | item no.3 | 2504 | sqm | 81.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.03 | Incoming | item no.3 |  |  | 1.03 | Two or more coats on new work | item no.3 | 2504 | sqm
1.04 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | item no.4 | 1183 | sqm | 108.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.04 | 2 No's 4000A, FP, EDO,50KA, ACB with microprocessor release (O/L, S/C & E/F protention) saftey shutter,SCM, CC, 4NO+4NC Aux. Contacts, interlock, shunt Trip contact T&C. etc. suitable to connect with the bus duct and through cables. ABB-Emax2/ Schneider MTZ/Siemens 3VA | item no.4 |  |  | 1.04 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | item no.4 | 1183 | sqm
1.05 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. | item no.5 | 1183 | sqm | 18.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.05 | breaker control switch TNC, Digital voltmeter/Ammeter Cl-1.0 with selector switch, Electronic KWH meter Cl-1.0, CT-4000/5A, Cl1.0, 15KVA cast rasin for metering, protection CTs 4000/5A, Cl-5P10, 15VA cast rasin IDMT relay , Trip circuit supervision relay , Phase indicating Lamp LED Type"Red, Tellow, Blue" Auto / Amnual selector switch Auxiliary contactors with 2NO+2NC , 2A SP MCB 10KA for cont. CKT. | item no.5 |  |  | 1.05 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. | item no.5 | 1183 | sqm
1.06 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : | item no.6 | [52 empty] | 1.06 | Both Incomer shall have class-b SPD of DEHN make. With 50KA 40A MPCB Protection. | item no.6 |  |  | 1.06 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : | item no.6
1.07 | One or more coats on old work | item no.7 | 84 | sqm | 75.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.07 | Bus bar: 1 No.4000 A, 50HZ, FP, Aliminium Bus Bar | item no.7 |  |  | 1.07 | One or more coats on old work | item no.7 | 84 | sqm
1.08 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade | item no.8 | [52 empty] | 1.08 | OutGoing: | item no.8 |  |  | 1.08 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade | item no.8
1.09 | Old work (one or more coats applied @ 0.83 ltr/10 sqm). | item no.9 | 437 | sqm | 64.96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.09 | 2 nos.2500 A, FP, EDO, 50 kA ACB with MPR based release (O/L, S/C & E/F protection) safety shutter, Aux. contacts 4NONC-2Nos, Breaker control switch TNC- 2Nos. 2A SP MCB 10KA for cont. CKT- 2nos. | item no.9 |  |  | 1.09 | Old work (one or more coats applied @ 0.83 ltr/10 sqm). | item no.9 | 437 | sqm
1.1 | WATER SUPPLY | item no.10 | [52 empty] | 1.1 | 2 nos.1600 A, FP, EDO, 50 kA ACB with MPR based release (O/L, S/C & E/F protection) safety shutter, Aux. contacts 4NONC-2Nos, Breaker control switch TNC- 2Nos. 2A SP MCB 10KA for cont. CKT- 2nos. | item no.10 |  |  | 1.1 | WATER SUPPLY | item no.10
1.11 | Repainting G.I. pipes and fittings with synthetic enamel white paint with one coat of approved quality : | item no.11 | [52 empty] | 1.11 | 3 nos. 800 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-3Nos, FP Spreader(8x3=24Nos) for MCCB 800A- 3 Nos | item no.11 |  |  | 1.11 | Repainting G.I. pipes and fittings with synthetic enamel white paint with one coat of approved quality : | item no.11
1.12 | 25 mm diameter pipe | item no.12 | 161 | metre | 10.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.12 | 2 nos. 630 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-2Nos, FP Spreader(8x2=16Nos) for MCCB 630A- 2Nos | item no.12 |  |  | 1.12 | 25 mm diameter pipe | item no.12 | 161 | metre
1.13 | NEW TECHNOLOGIES AND MATERIALS | item no.13 | [52 empty] | 1.13 | 4 nos. 400 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism-4Nos, FP Spreader(8x4=32Nos) for MCCB 400A- 4 Nos | item no.13 |  |  | 1.13 | NEW TECHNOLOGIES AND MATERIALS | item no.13
1.14 | Providing, mixing and applying bonding coat of approved adhesive on chipped portion of RCC as per specifications and direction of Engineer-In-charge complete in all respect. | item no.14 | [52 empty] | 1.14 | all out goings with ON.OFF, Trip, Spring charge indication.communicable type Digital multifunction energy meter(RS 485).Digital Amp meter with selector switches etc. | item no.14 |  |  | 1.14 | Providing, mixing and applying bonding coat of approved adhesive on chipped portion of RCC as per specifications and direction of Engineer-In-charge complete in all respect. | item no.14
1.15 | SBR Polymer (@10% of cement weight) modified cementitious bond coat @ 2.2 kg cement per sqm of surface area mixed with specified proportion of approved polymer | item no.15 | 182 | sqm | 103.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.15 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired up to terminal block. | item no.15 | 1 | No. | 1.15 | SBR Polymer (@10% of cement weight) modified cementitious bond coat @ 2.2 kg cement per sqm of surface area mixed with specified proportion of approved polymer | item no.15 | 182 | sqm
1.16 | Providing, mixing and applying SBR polymer (of approved make) modified Cement mortar in proportion of 1:4 (1 cement: 4 graded coarse sand with polymer minimum 2% by wt. of cement used) as per specifications and directions of Engineer-in-charge. Note: Measurement and payment: The pre-measurement of thickness shall be done just after the surface preparation is completed and Payment under this item shall be made only after proper wet curing has been done and surface has been satisfactorily evaluated by sounding / tapping with a blunt metal instrument and/or the 75mm size cube crushing strength at the end of 28 days to be not less than 30 N/Sqmm2). | item no.16 | [52 empty] | 1.16 | Supply installation testing and commissioning of cubical type DG set LT panel -2 (IEC 61439), suitable for 1600 Amp 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | item no.16 |  |  | 1.16 | Providing, mixing and applying SBR polymer (of approved make) modified Cement mortar in proportion of 1:4 (1 cement: 4 graded coarse sand with polymer minimum 2% by wt. of cement used) as per specifications and directions of Engineer-in-charge. Note: Measurement and payment: The pre-measurement of thickness shall be done just after the surface preparation is completed and Payment under this item shall be made only after proper wet curing has been done and surface has been satisfactorily evaluated by sounding / tapping with a blunt metal instrument and/or the 75mm size cube crushing strength at the end of 28 days to be not less than 30 N/Sqmm2). | item no.16
1.17 | 50 mm average thickness in 3 layers. | item no.17 | 182 | sqm | 895.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.17 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser/meter to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification. | item no.17 |  |  | 1.17 | 50 mm average thickness in 3 layers. | item no.17 | 182 | sqm
1.18 | MINOR CIVIL MAINTENANCE WORK. | item no.18 | [52 empty] | 1.18 | Incoming | item no.18 |  |  | 1.18 | MINOR CIVIL MAINTENANCE WORK. | item no.18
1.19 | Applying Fosroc Nitozink primer STD coat on corroded steel bars as per manufacturer specification. | item no.19 | 182 | Sqm | 145.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.19 | 3 No's 1250A, FP, 50KA, 4 pole ACB ( for 3x750 KVA SG sets) with microprocessor release (O/L, S/C & E/F protention) saftey shutter,SCM, CC, 4NO+4NC Aux. Contacts, interlock, shunt Trip contact T&C. etc. with 2 nos. 1250 A bus coupler (DG1 & DG2) (DG2-DG3) with all protections and metering. | item no.19 |  |  | 1.19 | Applying Fosroc Nitozink primer STD coat on corroded steel bars as per manufacturer specification. | item no.19 | 182 | Sqm
1.2 | EARTH WORK | item no.20 | [52 empty] | 1.2 | breaker control switch TNC, Digital voltmeter/Ammeter Cl-1.0 with selector switch, Electronic KWH meter Cl-1.0, CT-1250/5A, Cl1.0, 15VA cast rasin for metering, protection CTs 1250/5A, Cl-5P10, 15VA cast rasin IDMT relay , Trip circuit supervision relay , Phase indicating Lamp LED Type"Red, Tellow, Blue" Auto / Amnual selector switch Auxiliary contactors with 2NO+2NC , 2A SP MCB 10KA for cont. CKT. | item no.20 |  |  | 1.2 | EARTH WORK | item no.20
1.21 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : | item no.21 | [52 empty] | 1.21 | All the Incomer shall have class-b SPD of DEHN make. With 50KA 40A MPCB Protection. | item no.21 |  |  | 1.21 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : | item no.21
1.22 | All kinds of soil | item no.22 | [52 empty] | 1.22 | Bus bar: 1 No.1600 A, 50HZ, FP, Aliminium Bus Bar | item no.22 |  |  | 1.22 | All kinds of soil | item no.22
1.23 | Pipes, cables etc. exceeding 80 mm dia. But not exceeding 300 mm dia | item no.23 | 20 | metre | 365.94 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.23 | OutGoing: | item no.23 |  |  | 1.23 | Pipes, cables etc. exceeding 80 mm dia. But not exceeding 300 mm dia | item no.23 | 20 | metre
1.24 | STEEL WORK | item no.24 | [52 empty] | 1.24 | 3 nos. 800 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism- 3Nos, 2A SP MCB for cont. CKT.- 3 Nos | item no.24 |  |  | 1.24 | STEEL WORK | item no.24
1.25 | Providing and fixing hand rail of approved size by welding etc. to steel ladder railing, balcony railing, staircase railing and similar works, including applying priming coat of approved steel primer. | item no.25 | [52 empty] | 1.25 | 8 nos. 400 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection, rotary operated handle mechanism- 8Nos, 2A SP MCB for cont. CKT.- 8 Nos | item no.25 |  |  | 1.25 | Providing and fixing hand rail of approved size by welding etc. to steel ladder railing, balcony railing, staircase railing and similar works, including applying priming coat of approved steel primer. | item no.25
1.26 | M.S. tube | item no.26 | 2 | kg | 137.79 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.26 | 4 nos. 250 A, FP, 36 kA,MCCB with thermomagnetic release O/C,S/C protection - 3nos, rotary operated handle mechanism-4Nos, FP Spreader for MCCB 250A- 4 Nos | item no.26 |  |  | 1.26 | M.S. tube | item no.26 | 2 | kg
1.27 | FLOORING | item no.27 | [52 empty] | 1.27 | all outgoings with ON,OFF,Trip, spring charge indication. Communicable Digital multifunction energy meter(RS 485) . Digital Amp meter with selector switches etc. | item no.27 |  |  | 1.27 | FLOORING | item no.27
1.28 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : | item no.28 | [52 empty] | 1.28 | Note : All ACBs and MCCB's aux. contacts for ON/OFF and trip spare contacts to be wired up to terminal block. | item no.28 | 1 | Nos. | 1.28 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : | item no.28
1.29 | 25 mm thick | item no.29 | 15 | sqm | 1496.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.29 | S&I, testing & commissioning 4000 amp TPN aluminum bus duct with MS enclosure, as pe r enclosed specifications E-02. | item no.29 | 15 | Mtr. | 1.29 | 25 mm thick | item no.29 | 15 | sqm
1.3 | Dismantling and Demolishing | item no.30 | [52 empty] | 1.3 | S&I, testing & commissioning 4000amp TPN copper flexible links to connect tranformer LT bus duct as per enclosed specifications E-02. | item no.30 | 1 | Set | 1.3 | Dismantling and Demolishing | item no.30
1.31 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | item no.31 | [52 empty] | 1.31 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | item no.31 | 5 | Nos. | 1.31 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | item no.31
1.32 | Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | item no.32 | 30 | cum | 1759.83 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.32 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | item no.32 | 100 | Mtr. | 1.32 | Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | item no.32 | 30 | cum
1.33 | Nominal concrete 1:4:8 or leaner mix (i/c equivalent design mix) | item no.33 | 1.5 | cum | 1086.89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.33 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | item no.33 |  |  | 1.33 | Nominal concrete 1:4:8 or leaner mix (i/c equivalent design mix) | item no.33 | 1.5 | cum
1.34 | Dismantling stone slab flooring laid in cement mortar including stacking of serviceable material and disposal of unserviceable material within 50 metres lead. | item no.34 | 15 | sqm | 192.68 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.34 | 3½ X 400 sq. mm (82mm) | item no.34 | 50 | Nos. | 1.34 | Dismantling stone slab flooring laid in cement mortar including stacking of serviceable material and disposal of unserviceable material within 50 metres lead. | item no.34 | 15 | sqm
1.35 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved. | item no.35 | 32 | cum | 192.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.35 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | item no.35 |  |  | 1.35 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved. | item no.35 | 32 | cum
1.36 | ROAD WORK | item no.36 | [52 empty] | 1.36 | 3½ X 300 sq. mm | item no.36 | 4 | Nos. | 1.36 | ROAD WORK | item no.36
1.37 | Providing and laying design mix cement concrete of M-30 grade, in roads/ taxi tracks/ runways, using cement content as per design mix, using coarse sand and graded stone aggregate of 40 mm nominal size in appropriate proportions as per approved & specified design criteria, providing dowel bars with sleeve/ tie bars wherever required, laying at site, spreading and compacting mechanically by using needle and surface vibrators, levelling to required slope/ camber, finishing with required texture, including steel form work with sturdy M.S. channel sections, curing, making provision for contraction/ expansion, construction & longitudinal joints (10 mm wide x 50 mm deep) by groove cutting machine, providing and filling joints with approved joint filler and sealants, complete all as per direction of Engineer-in-charge (Item of joint fillers, sealants, dowel bars with sleeve/ tie bars to be paid separately). | item no.37 | [52 empty] | 1.37 | 3½ X 400 sq. mm | item no.37 | 4 | Nos. | 1.37 | Providing and laying design mix cement concrete of M-30 grade, in roads/ taxi tracks/ runways, using cement content as per design mix, using coarse sand and graded stone aggregate of 40 mm nominal size in appropriate proportions as per approved & specified design criteria, providing dowel bars with sleeve/ tie bars wherever required, laying at site, spreading and compacting mechanically by using needle and surface vibrators, levelling to required slope/ camber, finishing with required texture, including steel form work with sturdy M.S. channel sections, curing, making provision for contraction/ expansion, construction & longitudinal joints (10 mm wide x 50 mm deep) by groove cutting machine, providing and filling joints with approved joint filler and sealants, complete all as per direction of Engineer-in-charge (Item of joint fillers, sealants, dowel bars with sleeve/ tie bars to be paid separately). | item no.37
1.38 | Cement concrete prepared with batch mixing machine | item no.38 | 15 | cum | 8323.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.38 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc. as required | item no.38 |  |  | 1.38 | Cement concrete prepared with batch mixing machine | item no.38 | 15 | cum
1.39 | DRAINAGE | item no.39 | [52 empty] | 1.39 | 100 mm Dia | item no.39 | 50 | Mtr. | 1.39 | DRAINAGE | item no.39
1.4 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete : | item no.40 | [52 empty] | 1.4 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels | item no.40 | 2 | Cum | 1.4 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete : | item no.40
1.41 | 150 mm dia. R.C.C. pipe | item no.41 | 20 | metre | 432.35 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.41 | Providing 15 mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels. | item no.41 | 5 | Sqm | 1.41 | 150 mm dia. R.C.C. pipe | item no.41 | 20 | metre
1.42 | Constructing brick masonry road gully chamber 50x45x60 cm with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) including 500x450 mm pre-cast R.C.C. horizontal grating with frame complete as per standard design : | item no.42 | [52 empty] | 1.42 | Supplying and laying of one no. 4 C x 4.0 sq.mm. XLPE steel armoured copper conductor power cable of grade 1.1 kV as per following details. | item no.42 |  |  | 1.42 | Constructing brick masonry road gully chamber 50x45x60 cm with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) including 500x450 mm pre-cast R.C.C. horizontal grating with frame complete as per standard design : | item no.42
1.43 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | item no.43 | 6 | each | 4900.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.43 | Direct in ground including excavation, sand cushioning, protective covering and refilling the trench as reqd. | item no.43 | 30 | Mtr. | 1.43 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | item no.43 | 6 | each
1.44 | MINOR CIVIL MAINTENANCE WORK: | item no.44 | [52 empty] | 1.44 | In the existing RCC / HUME / STONE WARE / METAL pipe as reqd. | item no.44 | 30 | Mtr. | 1.44 | MINOR CIVIL MAINTENANCE WORK: | item no.44
1.45 | "Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:5:10 (1 cement : 5 coarse sand (zone-III) derived from natural sources: 10 graded brick aggregate 40 mm nominal size derived from natural sources) | item no.45 | 16.5 | Cum | 4985.93 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.45 | Direct in the existing masonry open duct as reqd. | item no.45 | 40 | Mtr. | 1.45 | "Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:5:10 (1 cement : 5 coarse sand (zone-III) derived from natural sources: 10 graded brick aggregate 40 mm nominal size derived from natural sources) | item no.45 | 16.5 | Cum
1.46 | Fixing kota stone strip with C.M 1:4 in C.C roads i/c cutting the cota stone in strips. | item no.46 | 110 | Rm | 15.78 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.46 | Supplying and laying chequered plate in cut pcs of 6mm thick with handle cutting/ welding as required complete. | item no.46 | 5 | Sqr. Mtr. | 1.46 | Fixing kota stone strip with C.M 1:4 in C.C roads i/c cutting the cota stone in strips. | item no.46 | 110 | Rm
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Total in Figures |  | 29911889
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE! | [5 empty] | Quoted Rate in Figures |  | Excess (+)
Quoted Rate in Words | [59 empty] | Quoted Rate in Words |  | INR Zero Only
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information