## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: SITC/ Replacement of 2 x 450 TR Induced Draft type Cooling Tower- 2 and 3 including associated works at ACMS central AC plant, IIT Kanpur
NIT No: HVAC/26/08/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component
1.01 | Induced Draft Counter FlowType Cooling Tower | item no.1 | [52 empty] | 1.01 | Induced Draft Counter FlowType Cooling Tower | item no.1 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | S/Replacement of Single cell, FRP type Min. 450 TR Induced draft-Counter flow Cooling tower (CT) of MSHDG (Mild Steel hot deep Galvanised) body frame, Safety net for fan-deck with SS nuts-bolts & washer of existing Square shape/size approx. 4550 x 4400 x 5250 mm (LxWxH) with Direct drive fan, TEFC IE-3/ IE5 Motor with class-F Insulation & IP-55/65 class protection, EN-8 fan-shaft with direct drive set mechanism, FRP axial fan blades assembly with SS hub with microcellular polyurethane based vibration isolators. The cooling tower fan-motor shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Heat rejection capacity of Cooling tower should be approx 67, 49,500 BTUs/hr or higher .The FRP Cooling Tower shall be factory fabricated with FRP Basin min. 05 mm thick and Body panel's min. 04 mm thick, UPVC with FRP lined/coated water distribution header & branches line system as per the specifications along with 250 mm inlet/outlet connection, 50 mm drainage/ over flow, 32 mm makeup/quick fills with float valve & equalizer line connection, PVC fills, louvers, Eurovent certified drift eliminators etc. The FRP panels and base shall be unsaturated polyester resin with UV protected gel coat. The tower fills & drift eliminator shall be UV protected high efficiency low clog uPVC virgin PVC type. The rate includes successful testing, commissioning of the cooling tower as per specification. | item no.2 | [52 empty] | 1.02 | S/Replacement of Single cell, FRP type Min. 450 TR Induced draft-Counter flow Cooling tower (CT) of MSHDG (Mild Steel hot deep Galvanised) body frame, Safety net for fan-deck with SS nuts-bolts & washer of existing Square shape/size approx. 4550 x 4400 x 5250 mm (LxWxH) with Direct drive fan, TEFC IE-3/ IE5 Motor with class-F Insulation & IP-55/65 class protection, EN-8 fan-shaft with direct drive set mechanism, FRP axial fan blades assembly with SS hub with microcellular polyurethane based vibration isolators. The cooling tower fan-motor shall be suitable for operation on 415±10% Volts, 50 Hz, 3 Phase AC power supply. Heat rejection capacity of Cooling tower should be approx 67, 49,500 BTUs/hr or higher .The FRP Cooling Tower shall be factory fabricated with FRP Basin min. 05 mm thick and Body panel's min. 04 mm thick, UPVC with FRP lined/coated water distribution header & branches line system as per the specifications along with 250 mm inlet/outlet connection, 50 mm drainage/ over flow, 32 mm makeup/quick fills with float valve & equalizer line connection, PVC fills, louvers, Eurovent certified drift eliminators etc. The FRP panels and base shall be unsaturated polyester resin with UV protected gel coat. The tower fills & drift eliminator shall be UV protected high efficiency low clog uPVC virgin PVC type. The rate includes successful testing, commissioning of the cooling tower as per specification. | item no.2
1.03 | a. Max. wet bulb temperature : 83 F (28.3C) | item no.3 | [52 empty] | 1.03 | a. Max. wet bulb temperature : 83 F (28.3C) | item no.3 |  |  | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | b. Temperature of water | item no.4 | [52 empty] | 1.04 | b. Temperature of water | item no.4
1.05 | Entering cooling tower : App. 97.52 F (36.4 C) | item no.5 | [52 empty] | 1.05 | Entering cooling tower : App. 97.52 F (36.4 C) | item no.5 |  |  | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | c. Temperature of water | item no.6 | [52 empty] | 1.06 | c. Temperature of water | item no.6
1.07 | Leaving cooling tower : App. 90 F (32.2 C) | item no.7 | [52 empty] | 1.07 | Leaving cooling tower : App. 90 F (32.2 C) | item no.7
1.08 | d. Water flow rate per tower : Min.1800 USGPM | item no.8 | [52 empty] | 1.08 | d. Water flow rate per tower : Min.1800 USGPM | item no.8
1.09 | e. Minimum efficiency of motors : Min.90% | item no.9 | [52 empty] | 1.09 | e. Minimum efficiency of motors : Min.90% | item no.9
1.1 | Single cell cooling towers as described above. | item no.10 | 2 | No | 1212790 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.1 | Single cell cooling towers as described above. | item no.10 | 2 | No | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.11 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | item no.11 | [52 empty] | 1.11 | Supplying, fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. Note:-The Pipes size 150mm & below shall be M.S. ‘C’ class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | item no.11
1.12 | 250 mm | item no.12 | 4 | Rmt. | 5833 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.12 | 250 mm | item no.12 | 4 | Rmt. | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | Finishing with Epoxy paint (two or more coats) at complete MSHDG ( Mild steel hot deep galvanized ) stucture,supporting Jali, MS base,I-beam etc of 450/500 TR of as per specifications complete as required. | item no.13 | 2 | jobs | 4504 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.13 | Finishing with Epoxy paint (two or more coats) at complete MSHDG ( Mild steel hot deep galvanized ) stucture,supporting Jali, MS base,I-beam etc of 450/500 TR of as per specifications complete as required. | item no.13 | 2 | jobs | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.14 | Structural Steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | item no.14 | [52 empty] | 1.14 | Structural Steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | item no.14
1.15 | I-Beam (100 mm x 50 mm) | item no.15 | 270 | Kg | 82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.15 | I-Beam (100 mm x 50 mm) | item no.15 | 270 | Kg
1.16 | Dismantling & removing of Existing old/defective Cooling Tower (CT) with associated parts i.e. disconnecting from CDW pipe lines, Motor, Gear box, Fan blades, FRP panel, fills , PVC pipes, Nozzles, GI/MS Structure, Valve/Strainer etc and taken out only FRP/PVC Scrap waste material excluding Motor, Gear box, GI/MS Structure etc from site and depositing/dump at designated location by municipal corporation outside of IITK complete as reqd. This item will be paid only with the prrof of proper dumping at dumping location as per SWM rules. | item no.16 | 2 | jobs | 5250 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.16 | Dismantling & removing of Existing old/defective Cooling Tower (CT) with associated parts i.e. disconnecting from CDW pipe lines, Motor, Gear box, Fan blades, FRP panel, fills , PVC pipes, Nozzles, GI/MS Structure, Valve/Strainer etc and taken out only FRP/PVC Scrap waste material excluding Motor, Gear box, GI/MS Structure etc from site and depositing/dump at designated location by municipal corporation outside of IITK complete as reqd. This item will be paid only with the prrof of proper dumping at dumping location as per SWM rules. | item no.16 | 2 | jobs
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K23: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K25: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K26: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K28: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K29: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information