## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: SITC of VRF Air Conditioning system and associated works including the buyback of existing (8 x 14 HP) VRF system in New Core Lab Building, IIT Kanpur
NIT No: HVAC/22/03/2024-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | OUTDOOR UNITS | item no.1 | [52 empty] | 1 | OUTDOOR UNITS | item no.1
2 | Supply, installation, testing and commissioning of air cooled Variable refrigerant volume /Variable refrigerant flow air conditioning system suitable for cooling and heating by using all inverter driven scroll compressors complete with indoor and outdoor units with individual controller and with all fittings and accessories etc complete in all respect as required . Installation shall include unloading, lifting and shifting of all machines and all associated material to roof top, all type of field wiring, power wiring and control wiring to out door units,between out door and indoor units and power wiring from main DB to all indoor and out door units as per site requirement complete with all minor civil work as required as per given specifications and having following items: Supply of (Cooling & Heating), with Single scroll inverter compressors, to be able to work till 56 degree centigrade, and work with flexible to operate even under extreme low load condition i.e less than 20 % . It should come with special pre- coated fins, panel, corrosion resistant & hydrophilic treatment coated condenser, electrical & microprocessor panel, isolating valves, factory gas charged for proper functioning of the units, full charge of refrigerant gas (R-410a), having following approximate capacities. with the criteria of non stop cooling up-to -10 to 56 degree Centigrade. Refrigerant cooled inverter drive. ODU should be site discharge only, Capacity as listed below. (Compatable with existing Bluestar make ductable indoor units) | item no.2 | [52 empty] | 2 | Supply, installation, testing and commissioning of air cooled Variable refrigerant volume /Variable refrigerant flow air conditioning system suitable for cooling and heating by using all inverter driven scroll compressors complete with indoor and outdoor units with individual controller and with all fittings and accessories etc complete in all respect as required . Installation shall include unloading, lifting and shifting of all machines and all associated material to roof top, all type of field wiring, power wiring and control wiring to out door units,between out door and indoor units and power wiring from main DB to all indoor and out door units as per site requirement complete with all minor civil work as required as per given specifications and having following items: Supply of (Cooling & Heating), with Single scroll inverter compressors, to be able to work till 56 degree centigrade, and work with flexible to operate even under extreme low load condition i.e less than 20 % . It should come with special pre- coated fins, panel, corrosion resistant & hydrophilic treatment coated condenser, electrical & microprocessor panel, isolating valves, factory gas charged for proper functioning of the units, full charge of refrigerant gas (R-410a), having following approximate capacities. with the criteria of non stop cooling up-to -10 to 56 degree Centigrade. Refrigerant cooled inverter drive. ODU should be site discharge only, Capacity as listed below. (Compatable with existing Bluestar make ductable indoor units) | item no.2
3 | ODU 14HP (nominal or higher capacity) | item no.3 | 8 | Nos | 295000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | ODU 14HP (nominal or higher capacity) | item no.3 | 8 | Nos
4 | INDOOR UNITS | item no.4 | [52 empty] | 4 | INDOOR UNITS | item no.4
5 | Supply, Installation, testing and commissioning of Cassette Type Indoor units equipped with, pre-filter, fan section with suitable static fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, drain pump, , unit should include insulation, pipe connections, variable evaporative temperature control and with cordless remote etc. of various capacities as per specifications and drawings.Make - BlueStar or its equivelant ) | item no.5 | [52 empty] | 5 | Supply, Installation, testing and commissioning of Cassette Type Indoor units equipped with, pre-filter, fan section with suitable static fan, multispeed motor, coil section with DX coil, outer cabinet, drain pan, drain pump, , unit should include insulation, pipe connections, variable evaporative temperature control and with cordless remote etc. of various capacities as per specifications and drawings.Make - BlueStar or its equivelant ) | item no.5
6 | Cassette Type Indoor Units - 2TR | item no.6 | 4 | Nos | 43800 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 6 | Cassette Type Indoor Units - 2TR | item no.6 | 4 | Nos
7 | Cassette Type Indoor Units - 3TR | item no.7 | 3 | Nos | 49400 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 7 | Cassette Type Indoor Units - 3TR | item no.7 | 3 | Nos
8 | Cassette Type Indoor Units - 4TR | item no.8 | 3 | Nos | 50400 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 8 | Cassette Type Indoor Units - 4TR | item no.8 | 3 | Nos
9 | Y- joints for refrigerant piping (pair). | item no.9 | 10 | Nos | 7900 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 9 | Y- joints for refrigerant piping (pair). | item no.9 | 10 | Nos
10 | ODU Connection Kit | item no.10 | 4 | Job | 15000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 10 | ODU Connection Kit | item no.10 | 4 | Job
11 | Group Controller | item no.11 | 4 | Job | 22890 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 11 | Group Controller | item no.11 | 4 | Job
12 | Alteration of existing software with PCB replacment for existing ductable units. | item no.12 | 10 | Job | 5900 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 12 | Alteration of existing software with PCB replacment for existing ductable units. | item no.12 | 10 | Job
13 | PIPING & OTHER WORKS | item no.13 | [52 empty] | 13 | PIPING & OTHER WORKS | item no.13
14 | Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm/13mm thick closed cell elastomeric insulation in tubing form inclusive of glass cloth and UV treatment. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays. Entire refrigerant piping work be carried out in accordance with the specifications. Piping shall be of following sizes: Make: Rajco/Mandev/Mettube/Hariom/Totaline/Hitachi. | item no.14 | [52 empty] | 14 | Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping suitable for R 410a refrigerant of suitable size as required and duly insulated with 19mm/13mm thick closed cell elastomeric insulation in tubing form inclusive of glass cloth and UV treatment. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using GI ladder type cable trays. Entire refrigerant piping work be carried out in accordance with the specifications. Piping shall be of following sizes: Make: Rajco/Mandev/Mettube/Hariom/Totaline/Hitachi. | item no.14
15 | Pipe Size Min. Wall Insulation | item no.15 | [52 empty] | 15 | Pipe Size Min. Wall Insulation | item no.15
16 | Size (O.D.) Thickness Thickness | item no.16 | [52 empty] | 16 | Size (O.D.) Thickness Thickness | item no.16
17 | 41.3 mm 1.43 mm 19 mm | item no.17 | 5 | Rmt | 1950 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 17 | 41.3 mm 1.43 mm 19 mm | item no.17 | 5 | Rmt
18 | 34.9 mm 1.21 mm 19 mm | item no.18 | 5 | Rmt | 1600 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 18 | 34.9 mm 1.21 mm 19 mm | item no.18 | 5 | Rmt
19 | 28.6 mm 1.00 mm 19 mm | item no.19 | 5 | Rmt | 1100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 19 | 28.6 mm 1.00 mm 19 mm | item no.19 | 5 | Rmt
20 | 22.9 mm 1.00 mm 13 mm | item no.20 | 5 | Rmt | 710 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 20 | 22.9 mm 1.00 mm 13 mm | item no.20 | 5 | Rmt
21 | 19.1 mm 1.00 mm 13 mm | item no.21 | 10 | Rmt | 650 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 21 | 19.1 mm 1.00 mm 13 mm | item no.21 | 10 | Rmt
22 | 15.9 mm 1.00 mm 13 mm | item no.22 | 10 | Rmt | 580 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 22 | 15.9 mm 1.00 mm 13 mm | item no.22 | 10 | Rmt
23 | 12.7 mm 0.80 mm 13 mm | item no.23 | 10 | Rmt | 360 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 23 | 12.7 mm 0.80 mm 13 mm | item no.23 | 10 | Rmt
24 | 9.5 mm 0.80 mm 13 mm | item no.24 | 10 | Rmt | 290 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 24 | 9.5 mm 0.80 mm 13 mm | item no.24 | 10 | Rmt
25 | 6.4 mm 0.80 mm 13 mm | item no.25 | 10 | Rmt | 210 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 25 | 6.4 mm 0.80 mm 13 mm | item no.25 | 10 | Rmt
26 | Supply and laying of pvc insulated following size control cum transmission sheilded copper conductor cable between each indoor and out door in medium class in pvc conduit on surface complete as required.Wire: Havells/Anchor/Finolex/Polycab/RR Kabel .PVC Conduit: Cap/AKG/BEC/KEI/Polycab | item no.26 | [52 empty] | 26 | Supply and laying of pvc insulated following size control cum transmission sheilded copper conductor cable between each indoor and out door in medium class in pvc conduit on surface complete as required.Wire: Havells/Anchor/Finolex/Polycab/RR Kabel .PVC Conduit: Cap/AKG/BEC/KEI/Polycab | item no.26
27 | 2 C x 1.5 Sqm | item no.27 | 100 | Rmt | 150 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 27 | 2 C x 1.5 Sqm | item no.27 | 100 | Rmt
28 | GI Earthing | item no.28 | [52 empty] | 28 | GI Earthing | item no.28
29 | Supply and Installation of GI Strip/Wire of following sizes. on surface or in recess. | item no.29 | [52 empty] | 29 | Supply and Installation of GI Strip/Wire of following sizes. on surface or in recess. | item no.29
30 | 25 mm x 3 mm thick | item no.30 | 20 | Rmt | 150 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 30 | 25 mm x 3 mm thick | item no.30 | 20 | Rmt
31 | Electrical Cable: | item no.31 | [52 empty] | 31 | Electrical Cable: | item no.31
32 | Supply , Installation, Testing & commissioning of Electrical Cable for Indoor & Outdoor Units & also for Incoming Supply to Electrical Panel . | item no.32 | [52 empty] | 32 | Supply , Installation, Testing & commissioning of Electrical Cable for Indoor & Outdoor Units & also for Incoming Supply to Electrical Panel . | item no.32
33 | 4 Core x 10 Sqmm Copper Cable Armoured | item no.33 | 20 | Rmt | 690 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 33 | 4 Core x 10 Sqmm Copper Cable Armoured | item no.33 | 20 | Rmt
34 | 3 Core x 2.5 Sqmm Copper Cable Unarmoured | item no.34 | 20 | Rmt | 225 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 34 | 3 Core x 2.5 Sqmm Copper Cable Unarmoured | item no.34 | 20 | Rmt
35 | Supply & fixing of fire retardant single layer canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | item no.35 | 5 | SqM | 2395 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 35 | Supply & fixing of fire retardant single layer canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | item no.35 | 5 | SqM
36 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.36 | [52 empty] | 36 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.36
37 | 0.63 mm (24 g) | item no.37 | 10 | SqM | 958 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 37 | 0.63 mm (24 g) | item no.37 | 10 | SqM
38 | 0.80 mm (22 g) | item no.38 | 5 | SqM | 1107 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 38 | 0.80 mm (22 g) | item no.38 | 5 | SqM
39 | Providing & fixing of thermal insulation with aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with dentrite/adhesive etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. | item no.39 | [52 empty] | 39 | Providing & fixing of thermal insulation with aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with dentrite/adhesive etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. | item no.39
40 | 13 mm | item no.40 | 5 | SqM | 305 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 40 | 13 mm | item no.40 | 5 | SqM
41 | 16 mm | item no.41 | 10 | SqM | 419 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 41 | 16 mm | item no.41 | 10 | SqM
42 | P & F of acoustic insulation with open cell Nitrile rubber sheet(Accosound) super silence of following thickness, on existing surface with adhesive i/c nut, bolt washer as req on duct./AHU room etc. complete as required. | item no.42 | [52 empty] | 42 | P & F of acoustic insulation with open cell Nitrile rubber sheet(Accosound) super silence of following thickness, on existing surface with adhesive i/c nut, bolt washer as req on duct./AHU room etc. complete as required. | item no.42
43 | 10 mm | item no.43 | 5 | SqM | 979 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 43 | 10 mm | item no.43 | 5 | SqM
44 | 15 mm | item no.44 | 5 | SqM | 1443 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 44 | 15 mm | item no.44 | 5 | SqM
45 | Supply, installation, testing and commissioning of uPVC Pipe, complete with fittings, supports,U trap arrangement,Clean Plug and accessories for AHU/IDU as per specifications, drawings. | item no.45 | [52 empty] | 45 | Supply, installation, testing and commissioning of uPVC Pipe, complete with fittings, supports,U trap arrangement,Clean Plug and accessories for AHU/IDU as per specifications, drawings. | item no.45
46 | 25 mm dia (with 6mm Nitrile) | item no.46 | 5 | Rmt | 160 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 46 | 25 mm dia (with 6mm Nitrile) | item no.46 | 5 | Rmt
47 | 32 mm dia (with 6mm Nitrile) | item no.47 | 5 | Rmt | 180 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 47 | 32 mm dia (with 6mm Nitrile) | item no.47 | 5 | Rmt
48 | 50 mm dia (with 6mm Nitrile) | item no.48 | 10 | Rmt | 230 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 48 | 50 mm dia (with 6mm Nitrile) | item no.48 | 10 | Rmt
49 | Additional Gas Charging - For external Piping | item no.49 | 61 | Kg | 800 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 49 | Additional Gas Charging - For external Piping | item no.49 | 61 | Kg
50 | Dismantling and removal of old AC equipments ( outdoor units and Cassette A/C's) alongwith defective canvass connection , copper pipes with insulation & accessories from their position to Outside of the Building | item no.50 | 1 | Job | 68750 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 50 | Dismantling and removal of old AC equipments ( outdoor units and Cassette A/C's) alongwith defective canvass connection , copper pipes with insulation & accessories from their position to Outside of the Building | item no.50 | 1 | Job
51 | Buyback of old ODU & IDU units, copper piping , supports etc | item no.51 | 1 | Lot | 165000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 51 | Buyback of old ODU & IDU units, copper piping , supports etc | item no.51 | 1 | Lot
52 | ANNUAL COMPREHENSIVE MAINTENANCE OF THE INSTALLED VRF SYSTEM FOR 03 YEARS AFTER DLP | item no.52 | [52 empty] | 52 | ANNUAL COMPREHENSIVE MAINTENANCE OF THE INSTALLED VRF SYSTEM FOR 03 YEARS AFTER DLP | item no.52
53 | Annual Comprehensive Maintenance Contract for period for 03 years (after 1 year of DLP). The contract shall include all spares, cosumables & replacement of defective/damaged parts as required to run the complete VRF system of capacity 8 x 14 HP through OEM including quarterly preventive maintenance and attending the shutdown/ breakdown issues within 24 hours of intimation. | item no.53 | [52 empty] | 53 | Annual Comprehensive Maintenance Contract for period for 03 years (after 1 year of DLP). The contract shall include all spares, cosumables & replacement of defective/damaged parts as required to run the complete VRF system of capacity 8 x 14 HP through OEM including quarterly preventive maintenance and attending the shutdown/ breakdown issues within 24 hours of intimation. | item no.53
54 | For 3 years (36 Months) | item no.54 | 36 | month | 18666 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 54 | For 3 years (36 Months) | item no.54 | 36 | month
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | Total in Figures |  | 29911889
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE! | Quoted Rate in Figures |  | Excess (+)
Quoted Rate in Words |  | #VALUE! | [52 empty] | Quoted Rate in Words |  | INR Zero Only
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information